## Asset Register
AS/NZS 3760:2022 Test & Tag Asset Register
Free template. Next Due Date auto-calculates from Last Test Date + Interval. Overdue rows turn red, due-within-30-days turn amber.
Asset ID / Tag No | Description | Make / Model | Serial No | Site / Location | Class (I / II) | Environment | Interval (months) | Last Test Date | Next Due Date | Last Result | Tester Name | Tester Licence | Notes
TT-001 | Extension lead 15m | HPM EL15 | SN48213 | Site A - Level 2 | I | Construction/Demolition | 3 | 2026-04-02 |  | Pass | J. Nguyen | EW-118842 | Tag green
TT-002 | Angle grinder | Makita GA5030 | SN90011 | Workshop bay 3 | I | Factory/Workshop | 6 | 2025-12-15 |  | Pass | J. Nguyen | EW-118842
TT-003 | Office monitor PSU | Dell U2722 | SN77321 | Head office | II | Office/School | 12 | 2025-06-01 |  | Fail | J. Nguyen | EW-118842 | Cord damaged - removed from service
Formulas:
Next Due Date = IF(OR([Last Test Date]="",[Interval (months)]=""),"",EDATE([Last Test Date],[Interval (months)]))

## Test Log
Test Log - per-test detail records
Test Date | Asset ID / Tag No | Visual Inspection | Earth Continuity (ohms) | Insulation Resistance (Mohm) | Polarity | Leakage (mA) | Result | Tester Name | Notes

## AS-NZS 3760 Intervals
AS/NZS 3760:2022 - recommended inspect & test intervals
Guidance summary only. Confirm against the current AS/NZS 3760:2022 standard and your own documented risk assessment. Intervals may be shortened by a risk assessment but not lengthened beyond the standard.
Environment / Situation | Interval | Notes
Building, construction and demolition sites | 3 months | Harsh environment, equipment damage likely. Most frequent retest.
Factories, workshops, manufacturing, assembly, fabrication, warehouse | 6 months | Class I and Class II equipment. RCD operating-time / push-button at 12 months.
Commercial cleaning equipment | 6 months | Equipment moved and subject to wear.
Hire equipment | 3 months | Plus inspect before each hire. Test before initial hire.
Schools, offices, equipment subject to flexing or abuse | 12 months | Cord flexed or equipment moved during normal use.
Equipment NOT subject to flexing or abuse (e.g. server rooms, fixed setups) | 5 years | Low-risk, equipment not moved and cord not flexed.
Second-hand equipment for resale | Before sale | No ongoing retest period once sold to end user.
Repaired or serviced equipment | After repair | Test and tag after any repair or service before return to use.
Sources (publicly published interval guidance):
AS/NZS 3760:2022 In-Service Safety Inspection and Testing of Electrical Equipment
appliancetaggingservices.com.au/electrical-safety-standard
portableappliancetesters.com.au/blogs/appliance-testing-supplies-blog/test-tag-frequency

## How To Use
AS/NZS 3760:2022 Test & Tag Register - free template
1. Use the 'AS-NZS 3760 Intervals' sheet to pick the right interval for each environment.
2. In 'Asset Register', enter each asset, its Class, Environment, Interval and Last Test Date.
3. Next Due Date fills in automatically. Overdue rows go red, due within 30 days go amber.
4. Record each individual test in the 'Test Log' sheet.
5. Filter or sort the register by Next Due Date before each site visit.
This template is free to use and share. No sign-up needed for the file itself.
TagSheet (the app, coming soon) does this for you automatically:
- Retest-due email reminders so nothing lapses
- One-click client-branded compliance PDF per site
- Asset history and tester records, no spreadsheet to maintain
Built by TagSheet. See the page you downloaded this from to register interest.